## Conversion - Heat pumps
KPIs/Technologies | KPIs/Technologies |  |  |  | Conversion Technologies
[5 empty] | Heat pumps (Air to Air) |  |  | Heat pumps (Air to Water) |  |  | Heat pumps (Ground source)
|  |  | form | units | value | source | remark | value | source | remark | value | source | remark
Size | Size | Power (heating) | Range or average value | [kW] | 1 to 100 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | 1 to 100 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | 1 to 100 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | .
|  | Power (cooling) | Range or average value | [kW] | 1 to 100 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | 1 to 100 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | 1 to 100 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | .
| Costs | CAPEX (per unit of installed power capacity) | cost curve | [kCHF/kW] | 0.6 to 0.8 |  | for residential / small commercial | 0.8 to 1.0 |  | for residential / small commercial | 0.9 to 1.7 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | for residential / small commercial | .
|  | OPEX and maintainence per year | Range or average value | [kCHF/y] | - |  | included in the LCOH | - |  | included in the LCOH | - |  | included in the LCOH | .
|  | Levelized cost of heat/energy | cost curve | [CHF/MWh] | 110 to 130 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | 110 to 130 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | 115 to 150 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | .
Ageing / degradation | Ageing / degradation | Lifetime | Range or average value | [y] | 20 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | 20 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | 20 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | .
|  | Minimum time to failure | Range or average value | [y] | 10 | https://termo-plus.com/blog/life-expectancy-of-heat-pumps/ | 99% of heat pumps last at least 10 years | 10 | https://termo-plus.com/blog/life-expectancy-of-heat-pumps/ | 99% of heat pumps last at least 10 years | 10 | https://termo-plus.com/blog/life-expectancy-of-heat-pumps/ | 99% of heat pumps last at least 10 years | .
|  | Maintainence frequency and duration | Range or average value | [occurrance/y] | [1/y] | https://gacservices.com/blog/time-schedule-heat-pump-tune-up/ |  | [1/y] | https://gacservices.com/blog/time-schedule-heat-pump-tune-up/ | not longer than 1 day | [1/y] | https://gacservices.com/blog/time-schedule-heat-pump-tune-up/ | not longer than 1 day | .
|  | Maintainence duration | Range or average value | [d] | < 1 day | https://gacservices.com/blog/time-schedule-heat-pump-tune-up/ |  | < 1 day | https://gacservices.com/blog/time-schedule-heat-pump-tune-up/ |  | < 1 day | https://gacservices.com/blog/time-schedule-heat-pump-tune-up/ |  | .
|  | Degradation Rate | Range or average value | [%/year¦ or [%/cycle] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Failure Rate | Range or average value | [failures/operating hour] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
Technical | Performance | Efficiency | Range or average value | [-] | see technology specific |  |  | see technology specific |  |  | see technology specific |  |  | .
|  | Technology Readiness Level | Value from 1-9 | [-] | 9 |  |  | 9 |  |  | 9 |  |  | .
|  | Auxiliary Losses | Range or average value | [%] (efficiency of aux) | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Standby Losses | Range or average value | [%power capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Footprint | Range or average value | [kW/m^2] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
| Flexibility characteristics | Ramping (Rate of Change) | Range or average value | [%/s] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Minimum Up/Down time | Range or average value | [minutes] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Response time (signal to activation) | Range or average value | [seconds] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Minimum Operating Level | Range or average value | [% of rated capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Availability for Flexibility Provision (any other limits) | Range or average value | [% of rated capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Controllability (share/capacity available for flexibility) | Range or average value | [% of rated capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Capacity Factor | Range or average value | % | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
| Technology specific | Efficiency (Coefficient of Performance, 40°C space heating) | Range or average value | [-] | 3.3 to 3.9 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | . | 3.3 to 3.9 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | . | 4.5 to 5.4 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | .
|  | Efficiency (Coefficient of Performance, 55°C hot water) | Range or average value | [-] | 2.3 to 2.8 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | . | 2.3 to 2.8 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | . | 3.1 to 3.8 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | .
|  | Efficiency (Coefficient of Performance, average) | Range or average value | [-] | 2.9 to 3.5 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | . | 2.9 to 3.5 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | . | 3.9 to 4.8 | https://pubs.rsc.org/en/content/articlehtml/2012/ee/c2ee22653g | .
|  | Operable temperature range (condenser) | Range or average value | [°C] | 32 to 65 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | High and Very High Temperature heat pumps capable of higher condenser temperatures (not covered here) | 32 to 65 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | High and Very High Temperature heat pumps capable of higher condenser temperatures (not covered here) | 32 to 65 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | High and Very High Temperature heat pumps capable of higher condenser temperatures (not covered here)
|  | Operable temperature range (evaporator) | Range or average value | [°C] | above -20 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | above -20 | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | . | * | https://www.sciencedirect.com/science/article/pii/S0378778821004825#s0050 | in accordance with local soil temperatures and their flucuation
| Emissions | Embodied emissions | Range or average value | [kgCO2/kW delivered] | * |  | estimated by taking kgCO2/kW of electricity consumed and dividing by COP | * |  | estimated by taking kgCO2/kW of electricity consumed and dividing by COP | * |  | estimated by taking kgCO2/kW of electricity consumed and dividing by COP | .
|  | Operating emissions | Range or average value | [10 empty] | .
system depdenent

## Conversion - Solar technologies
KPIs/Technologies | KPIs/Technologies
[5 empty] | PV |  |  | Solar Thermal |  |  | PVT
|  |  | form | units | value | source | remark | value | source | remark | value | source | remark
Size | Size | Power (heating) | Range or specific value | [kW] | 0 to 37500 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | range for documented cases of solar collectors connected to thermal energy storage | 0 to 37500 |  | comprable to PV | 0 to 37500 |  | comprable to ST | .
|  | Power (cooling) | Range or average value | [kW] | 1.6 to 2 | https://news.energysage.com/what-is-the-power-output-of-a-solar-panel/ | lower end of range for residential | 1.6 to 2 |  | comprable to PV | 1.6 to 2 |  | comprable to ST | .
| Costs | CAPEX (per unit of installed power capacity) | cost curve, empirically determined | [kCHF/kW] | 2 to 3 historically; 0.8 most recent lowest values | Trends in PV Applications 2022; https://www.irena.org/publications/2022/Jul/-/media/Files/IRENA/Agency/Publication/2022/Jul/IRENA_Power_Generation_Costs_2021_Summary.pdf?la=en&hash=C0C810E72185BB4132AC5EA07FA26C669D3AFBFC | residential systems | 820 * x + 7000 | https://www.energieschweiz.ch/tools/solarrechner/ | where x is the solar collector area in [m2] | 820 * x + 7000 | https://www.energieschweiz.ch/tools/solarrechner/ | comprable to PVT | .
|  | OPEX and maintainence per year | cost curve, empirically determined | [kCHF/y] | - | Trends in PV Applications 2022 | included in LCOE | 0.5 to 1.5 % | https://www.sciencedirect.com/science/article/pii/S0306261916315835 | of CAPEX | 0.5 to 1.5 % | https://www.sciencedirect.com/science/article/pii/S0306261916315835 | included in LCOE | .
|  | Delivered energy cost; levelized cost of heat/energy | cost curve, empirically determined | [CHF/MWh] | 150 to 250 historically; 48 most recent lowest values | Trends in PV Applications 2022; https://www.irena.org/publications/2022/Jul/-/media/Files/IRENA/Agency/Publication/2022/Jul/IRENA_Power_Generation_Costs_2021_Summary.pdf?la=en&hash=C0C810E72185BB4132AC5EA07FA26C669D3AFBFC | . | 230 to 506 | https://www.mdpi.com/2076-3417/10/14/4771 | price is [CHF/m2] | 205 to 210 | https://www.iea-shc.org/Data/Sites/1/media/events/webinars/2020-03-25/pvt-systems-kpis-dz.pdf | for both electricity and heat, value is an average across 11 systems, range goes up to 750 for LCOE and 510 for LCOH | .
Ageing / degradation | Ageing / degradation | Lifetime | Range or average value | [y] | 25 | https://www.sciencedirect.com/science/article/pii/S1110016821008334#f0005 | mono-crystalline silicon | 30 | https://www.sciencedirect.com/science/article/pii/S0306261916315835#s0035 |  | 30 | https://www.sciencedirect.com/science/article/pii/S0306261916315835#s0035 |  | .
|  | Minimum time to failure | Range or average value | [y] | 20 | Trends in PV Applications 2022 | . | 20 |  | comprable to PV | 20 |  | comprable to PV | .
|  | Maintainence frequency and duration | Range or average value | [occurrance/y] | n.a. |  | could not find information on this | n.a. |  | could not find information on this | n.a. |  | could not find information on this | .
|  | Maintainence duration | Range or average value | [d] | n.a. |  | could not find information on this | n.a. |  | could not find information on this | n.a. |  | could not find information on this | .
|  | Degradation Rate | Range or average value | [%/year¦ or [%/cycle] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Failure Rate | Range or average value | [failures/operating hour] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
Technical | Performance | Efficiency (nominal) | Range or average value | [-] | 14 to 20 | https://www.sciencedirect.com/science/article/pii/S1110016821008334#f0005 | mono-crystalline silicon | 85 to 87 | ASHRAE. (1995). ASHRAE handbook: heating, ventilating and air-conditioning APPLICATIONS 1995. American Society of Heating Refrigerating and Air-conditioning Engineers. |  | 12.2 to 44.5 ;5 to 20 for PV; 85 to 87 for ST | https://www.sciencedirect.com/science/article/pii/S0306261912008549#b0065; https://reader.elsevier.com/reader/sd/pii/S0038092X00001535?token=A707CB5F98A881AC6819DE4F28309B0422F7E5350929AF6C46AB1A1A110337376FB84E49238F0FA9014D57473209DE75&originRegion=eu-west-1&originCreation=20230430194843 | average for PVT; for PV module; ST | .
|  | Technology Readiness Level | Value from 1-9 | [-] | 9 |  |  | 4 to 8 | https://www.rhc-platform.org/content/uploads/2019/05/Solar_Thermal_Roadmap.pdf |  | 4 to 8 | https://www.rhc-platform.org/content/uploads/2019/05/Solar_Thermal_Roadmap.pdf
|  | Auxiliary Losses | Range or average value | [%] (efficiency of aux) | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Standby Losses | Range or average value | [%power capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Footprint | Range or average value | [kW/m^2] | n.a. |  | . | n.a. |  |  | n.a. |  |  | .
| Flexibility characteristics | Ramping (Rate of Change) | Range or average value | [%/s] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Minimum Up/Down time | Range or average value | [minutes] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Response time (signal to activation) | Range or average value | [seconds] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Minimum Operating Level | Range or average value | [% of rated capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Availability for Flexibility Provision (any other limits) | Range or average value | [% of rated capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Controllability (share/capacity available for flexibility) | Range or average value | [% of rated capacity] | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
|  | Capacity Factor | Range or average value | % | n.a. |  |  | n.a. |  |  | n.a. |  |  | .
| Technology specific | Power output per panel | Range or average value | [W/p] | 277 to 440 | https://news.energysage.com/what-is-the-power-output-of-a-solar-panel/ | . | 50 to 400 | https://pdf.sciencedirectassets.com/271459/1-s2.0-S0038092X00X04148/1-s2.0-S0038092X04000970/main.pdf?X-Amz-Security-Token=IQoJb3JpZ2luX2VjEIv%2F%2F%2F%2F%2F%2F%2F%2F%2F%2FwEaCXVzLWVhc3QtMSJIMEYCIQD1nu%2FPBv2SJjdK7qLoxoiD%2FPcSNRkFoewIr%2B8VsTqSwgIhANj1lcERPM2gld7qvE91%2FwO4nRg5vRuVbbIFvkXhkrIHKrsFCJT%2F%2F%2F%2F%2F%2F%2F%2F%2F%2FwEQBRoMMDU5MDAzNTQ2ODY1IgwkHpLKGdak%2Fs2V74EqjwUJ0jj9Ew91NlduUzZ4DCRx2M62SpvXG7ZAaERS9g3YoP3JdfaYHwkUwiHM9HyoQM3j%2BNxLTNI2YwyQZJVU%2FJmPIkbcP4Do7EVk0F1p48anOWnbSsXLY73hpnOsXs6Uny%2FiuIl2Wyt0HXiQx7rxHzDfVwoRQBBDVkxAtGIBWtaKyXAVKi%2BrB%2BYeER3aWzU9j2jAxpruegBg9jafbBuIw%2BUuRn0oncu8aeUeSBLQyHMl0YcjBymRmCq3xeKhryM6hn%2B925ewKXm57BMlTrgYIFXGyS%2BEidmUOi%2FUFXsuAuY7dHeYHeDae%2BdfA0aD5FhKeqmZVRJd0uNggxczKthZxoSImLJsq%2FYKN%2BcrpVaRW3ggt6t7WimTAaK3CxxOnv0LSU2P4WBRAiKPC4vpWynqZeBVNZ4TWdSElnwm58xz2im81xsGwg%2BLSurGRA9hEfeoDvj6i1w73W7Dx13pvX5kWrWdOziTvV%2FN%2BBILkpBV5p2E%2BoZ6lLeiisghz4raOqtfp5jEnTsZjkkgp093yYrkDXWTy9wC6xsgekBbzJaZiub1ExTlvrtnI0114fN9BJieuYS6dJ2Tqavhz8ZEaNEotf5DVN34sHWpuNMYwlbrkEYEnewcWjrxQ36ylA1ohrBsC0WONAQu%2Ff5bnYWHkTFf%2Fi3guxUwB3wa2Aa8qp%2BNx7013qeyOwVhVTsPGTwV%2FQ8nvnVn1V%2FFYrrEXZuISHOYmgTgFsi4Q%2Bz4b%2B0gRl1y5SmwxRpuCcvIPn5kZJ%2BE%2FcbIpkFRxmiaznRSbudtJx9q791ggbziYjs8Z6d2ouOCHHJZgrsiP8%2FvHyfHKr2ixzzHolWY0FQfbG1LQ05wnaP%2FZUrkHKUXPB3xbfkKBzZeW3QzMOPluqIGOrABOBWBXm1rAKY7XEq%2Bq%2F6jSdNwaehXdvXGIHRL4SBeBYGBd0U4CaZFkrjGJcV4U131knKYyXsBeSnqdyYdVWaZGHDu%2FOZxvYKarTv%2BUKFhNswOmxY39fYdF7VUP%2FkG3CR4kiN2TL5jOhxVOaF5d80VujbOMQGdxlvlToAZMuthHTYddokk2fsG2NN1J71jDnWZ7fA2vIwhR2voazblxzvSbWFd6emPUo5Q26l7E%2BrFUl8%3D&X-Amz-Algorithm=AWS4-HMAC-SHA256&X-Amz-Date=20230430T194156Z&X-Amz-SignedHeaders=host&X-Amz-Expires=300&X-Amz-Credential=ASIAQ3PHCVTYQCGHNCN4%2F20230430%2Fus-east-1%2Fs3%2Faws4_request&X-Amz-Signature=5f00a92d4b3cfec4329a0eb24a033215367ca6be0454bb1a0e75cc3bae0d2395&hash=94886e6f27db6a576476221ca72573eb9b718accc839c01561859f4a9943ac8b&host=68042c943591013ac2b2430a89b270f6af2c76d8dfd086a07176afe7c76c2c61&pii=S0038092X04000970&tid=spdf-288a799e-d67b-4174-8d3a-c763cebf2bc9&sid=d6fd6a314f4fd744235af5e-9e14043e0149gxrqb&type=client&tsoh=d3d3LnNjaWVuY2VkaXJlY3QuY29t&ua=050b5803545c5452005f&rr=7c0243d98e193b64&cc=ch | [kWh/m2/y] dependent on local irradiation
| Emissions | Embodied emissions | Range or average value | [kgCO2/kW delivered] | 0.05 to 0.2 | https://www.sciencedirect.com/science/article/pii/S0378778817323101#fig0001 |  | 0.025 | https://www.sciencedirect.com/science/article/pii/S0378778817323101#fig0001 |  | 0.025 | https://www.sciencedirect.com/science/article/pii/S0378778817323101#fig0001 |  | .
|  | Operating emissions | Range or average value | [10 empty] | .
system depdenent

## Storage - TES
KPIs/Technologies |  |  |  | Storage technologies
|  |  |  | Sensible - Water-based storage (Pressurised Tank) |  |  | Sensible - Water-based storage (seasonal - Tall Tank) |  |  | Sensible - Water-based storage (seasonal - Flat Tank) |  |  | Sensible - Aquifier (seasonal) |  |  | Sensible - Water-based storage (seasonal - Pit) |  |  | Sensible - BTES (seasonal) |  |  | Latent thermal storage |  |  | Thermal Grids
|  | form | units | value | source | remark | value | source | remark | value | source | remark | value | source | remark | value | source | remark | value | source | remark | value | source | remark | value | source | remark
Size | Storage volume range | Range or average value | [m3] | 100 to 10000 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | . | 200 to 50000 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 200 to 50000 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 20000 to 500000 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 1000 to 500000 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdbecken.pdf; Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 6000 to 500000 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches - ScienceDirect and http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf |  | 1 to 11.6 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | based on 2 active LTES systems | 6000 to 500000 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches - ScienceDirect and http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf | Comprable to BTES | .
| Energy capacity range | Range or average value | [MWh] | 160 to 28000 | https://www.sciencedirect.com/science/article/pii/S1364032121000290 | . | 20 to 5000 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 20 to 5000 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 400 to 20000 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 40 to 40000 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdbecken.pdf; Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 133 to 28000 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches - ScienceDirect and http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf, Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect |  | 0.016 to 0.32 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | based on 2 active LTES systems | 133 to 28000 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches - ScienceDirect and http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf, Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | Comprable to BTES | .
Costs | CAPEX per unit of storage capacity | cost curve, empirically determined | [CHF/MWh] | 685 to 5550 | https://www.sciencedirect.com/science/article/pii/S1364032121000290 | range of 3 TTES studies | 685 to 5550 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 685 to 5550 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | price per MWh in similar range for pressurised due to trade-off between energy density and cost per m3 | 54 (250-1500 from OST) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | data from only 1 ATES available | 1637.5 (375 to 5000 from OST values) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average of 4 PTES studies | 610 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | only data from 2 BTES available | 15000 to 360000 | https://www.sandia.gov/ess-ssl/wp-content/uploads/2020/12/ESHB_Ch12_Thermal_Ho.pdf; https://link.springer.com/book/10.1007/978-3-662-55504-0 | large uncertainty in values | 610 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | only data from 2 BTES available | .
| CAPEX per unit of storage capacity per cycle | cost curve, empirically determined | [CHF/MWh/cycle] | 685 to 5550 * x | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | assuming 52 cycles per year, with x equal to MWh*cycle | 685 to 5550 * x | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | assuming 1 cycle per year, with x equal to MWh*cycle | 685 to 5550 * x | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | assuming 1 cycle per year, with x equal to MWh*cycle | 54 * x (250-1500 from OST) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | assuming 1 cycle per year, with x equal to MWh*cycle | 1637.5 * x (375 to 5000 from OST values) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average of 4 PTES studies | 610 * x | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | assuming 1 cycle per year, with x equal to MWh*cycle | 15000 to 360000 * x | https://www.sandia.gov/ess-ssl/wp-content/uploads/2020/12/ESHB_Ch12_Thermal_Ho.pdf; https://link.springer.com/book/10.1007/978-3-662-55504-0 | Assuming 1 cycle per year, with x equal to MWh*cycle | 610 * x | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | assuming 1 cycle per year, with x equal to MWh*cycle | .
| CAPEX per unit of storage volume | cost curve, empirically determined | [CHF/m3] | 500 to 2'000 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | . | 400 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 220 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | at low end of cost range | 12.3 (10-30 from OST) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | averaged value over 3 ATES | 135 (OST values 30 to 200) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average of 6 PTES studies | 15.6 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | averaged value over 7 BTES | 250 to 1383 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk); Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | large uncertainty in values | 15.6 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | averaged value over 7 BTES | .
| CAPEX per unit of power capacity | cost curve, empirically determined | [kCHF/kW] | 3 | https://www.sciencedirect.com/science/article/pii/S1364032121000290 | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. | 3 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. | 3 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. | 0.24 (1.1 to 6.57 from OST values) | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. only data from 1 ATES available. | 1.64 to 21.9 from OST values | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. | 2.7 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. only data from 2 BTES available. | 0.08 to 0.16 | https://link.springer.com/book/10.1007/978-3-662-55504-0 | . | 2.7 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | calculated assuming the storage capacity discharged in half year, i.e. 8760/2 hours. only data from 2 BTES available. | .
| OPEX and maintainence per year | cost curve, empirically determined | [kCHF/y] | 1.51 | https://www.sciencedirect.com/science/article/pii/S1364032121000290 | average of 2 TTES studies | 1.5 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average of 2 TTES studies | 1.5 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 7.9 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 3 ATES | 21.4 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 3 PTES | 3.5 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 7 BTES | 0.1 to 0.5 | https://link.springer.com/book/10.1007/978-3-662-55504-0 | unit in [CHF/kWh] | 3.5 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 7 BTES | .
| Delivered energy cost; levelized cost of heat/energy | cost curve, empirically determined | [CHF/MWh] | 180 to 230 | https://www.sciencedirect.com/science/article/pii/S1364032121000290 | . | 212.7 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 212.7 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 121.8 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 3 ATES | 63 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 3 PTES | 203.6 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 7 BTES | 382.69 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | data from 1 LHS available | 203.6 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | average over 7 BTES | .
Ageing / degradation | Lifetime | Range or average value | [y] | 25-50 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | . | 25 to 50 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 25 to 50 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 20-30 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 20 to 30 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 25 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | based on existing BTES, recent studies estimate up to 60 years | 12 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect; https://link.springer.com/book/10.1007/978-3-662-55504-0 | limited data available. 5000 cycles (Handbook) | 25 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | based on existing BTES, recent studies estimate up to 60 years | .
| Self-discharge per day | Range or average value (tiered by storage temperature) | [%] | 1 |  | varies with storage temperature and degree of insulation; values in %, calculated from efficiency values assuming 1 week charge cycle | 0.24 to 0.33 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | values are %. Calculated from the range efficiency values and assuming a discharge time of 365/2 days | 0.24 to 0.33 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | 0.13 to 0.30 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | values are %. Calculated from the range efficiency values and assuming a discharge time of 365/2 days | 0.1 to 0.25 |  | values are %. Calculated from the range efficiency values and assuming a discharge time of 365/2 days | 0.2 to 0.4 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | values are %. Calculated from the range efficiency values and assuming a discharge time of 365/2 days | negligible |  |  | 0.2 to 0.4 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | values are %. Calculated from the range efficiency values and assuming a discharge time of 365/2 days | .
| Minimum time to failure | Range or average value | [y] | n.a. |  | comparable to heat exchangers and pressurised vessels | n.a. |  | comparable to heat exchangers | n.a. |  | comparable to heat exchangers | n.a. |  | comparable to underground heat exchangers and BTES | n.a. |  | comparable to heat exchangers | n.a. |  | could not find information on this. It can be compared though to ground heat exchangers | n.a. |  | Could not find information on this. It can be compared though to ground heat exchangers | n.a. |  | could not find information on this. It can be compared though to ground heat exchangers | .
| Maintainence frequency and duration | Range or average value | [-],[-] | min [1/y] [d] | https://www.nfpa.org/codes-and-standards/all-codes-and-standards/list-of-codes-and-standards/detail?code=25 | based on maintanence standards for pressurised water tanks in fire protection systems | n.a. |  | could not find information on this. It can be compared though to heat exchangers | n.a. |  | could not find information on this. It can be compared though to heat exchangers | n.a. |  | could not find information on this. It can be compared though to underground heat exchangers | n.a. |  | could not find information on this. It can be compared though to heat exchangers | n.a. |  | could not find information on this. It can be compared though to ground heat exchangers | n.a. |  | Could not find information on this. It can be compared though to ground heat exchangers | n.a. |  | could not find information on this. It can be compared though to ground heat exchangers | .
Performance | Energy density (gravimetric) | Range or average value | [kWh/kg] | 0.06 to 0.18 |  | calculated from volumetric | 0.04 to 0.08 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | from volumetric density assuming a water density of 1000 kg/m3 | 0.04 to 0.08 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | from volumetric density assuming a water density of 1000 kg/m3 | 0.02 to 0.04 | OST | from volumetric density assuming a water density of 1000 kg/m3 | 0.04 to 0.08 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | from volumetric density assuming a water density of 1000 kg/m3 | 0.015 | Factors influencing the performance of shallow Borehole Heat Exchanger - ScienceDirect | from volumetric density assuming a soil density of 1500 kg/m3 | 0.049 to 0.097 | https://link.springer.com/book/10.1007/978-3-662-55504-0 | . | 0.015 | Factors influencing the performance of shallow Borehole Heat Exchanger - ScienceDirect | from volumetric density assuming a soil density of 1500 kg/m3 | .
| Energy density (volumetric) | Range or average value | [kWh/m3] | 60 to 180 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | . | 40 to 80 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 40 to 80 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 20 to 40 | OST |  | 40 to 80 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 22.5 | http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf | . | 53.2 to 528 (113 from Handbook) | https://www.sandia.gov/ess-ssl/wp-content/uploads/2020/12/ESHB_Ch12_Thermal_Ho.pdf; https://link.springer.com/book/10.1007/978-3-662-55504-0 | assuming a denisty of 1900 kg/m3 for liquid sodium nitrate | 22.5 | http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf | . | .
| Power density | Range or average value | [kW/m3] | 357 to 1070 | https://www.engineeringtoolbox.com/water-thermal-properties-d_162.html | assuming the energy density discharged in 7 days | 9.17 to 18.3 | https://www.engineeringtoolbox.com/water-thermal-properties-d_162.html | assuming the energy density discharged in 365/2 days | 9.17 to 18.3 | https://www.engineeringtoolbox.com/water-thermal-properties-d_162.html | assuming the energy density discharged in 365/2 days | 4.6 to 9.17 |  | assuming the energy density discharged in 365/2 days | 9.17 to 18.3 |  | assuming the energy density discharged in 365/2 days | 3.44 |  | assuming the energy density discharged in 365/2 days | 4.7 | https://link.springer.com/book/10.1007/978-3-662-55504-0 | Assuming the energy density discharged in 1 day (using Handbook value of volumetric energy density) | 3.44 |  | assuming the energy density discharged in 365/2 days | .
| Power rating range | Range or average value | kW | 0 to 140 | https://www.engineeringtoolbox.com/water-thermal-properties-d_162.html | assuming x hour discharge time, 0-120 deg drop, 4.18 kJ/kgK | 0 to 100 | https://www.engineeringtoolbox.com/water-thermal-properties-d_162.html | assuming x hour discharge time, 0-88 deg drop, 4.18 kJ/kgK | 0 to 100 | https://www.engineeringtoolbox.com/water-thermal-properties-d_162.html | assuming x hour discharge time, 0-88 deg drop, 4.18 kJ/kgK | 0 to 100 |  | assuming x hour discharge time, 0-70 deg drop, 4.18 kJ/kgK | 0 to 100 |  | assuming x hour discharge time, 0-85 deg drop, 4.18 kJ/kgK | 0 to 100 |  |  | - |  | typically low due to low thermal conductivity values | 0 to 100 |  |  | .
| Round trip efficiency | Range or average value | [%] | 80 to 90 | https://www.sciencedirect.com/science/article/pii/S1364032121000290; https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/545249/DELTA_EE_DECC_TES_Final__1_.pdf | . | 80 to 90 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | 80 to 90 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | 46 to 77 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | 55 to 82 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 0.2 to 0.65 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | 40 to 90 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk); Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | 0.2 to 0.65 | Seasonal thermal energy storage: A techno-economic literature review ¦ Elsevier Enhanced Reader | . | .
| Technology Readiness Level | Value from 1-9 | [-] | 9 | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/545249/DELTA_EE_DECC_TES_Final__1_.pdf | . | 9 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 9 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 5 to 8 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 6 to 8 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 6 to 8 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | values for underground thermal energy storage | 5 to 8 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 6 to 8 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | values for underground thermal energy storage | .
Flexibility characteristics | Maximum charging power | Range or average value | [kW] | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  |  | n.a. |  | limited by thermal conductivity of PCM matrix | n.a. |  |  | .
| Maximum discharging power | Range or average value | [kW] | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  | dependent on operational variables | n.a. |  |  | n.a. |  | dependent on PCM matrix and heat transfer surface structure | n.a. |  |  | .
| Minimum operational capacity | Range or average value | [%] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | 0 |  |  | 0 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | .
| Number of cycles per year | Range or average value | [-] | 1+ |  | typically used in multiple cycles per year | 1 to 2 |  | typically used in multiple cycles per year | 1 to 2 |  | typically used in multiple cycles per year | 0.41 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches ¦ Elsevier Enhanced Reader | only data from 1 ATES available | 1 to 2 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 1 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches ¦ Elsevier Enhanced Reader | . | 365+ | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 1 | Seasonal thermal energy storage in smart energy systems: District-level applications and modelling approaches ¦ Elsevier Enhanced Reader | . | .
| Response time | Range or average value | [mins] | 1+ |  | larger tanks will respond slower | 1+ |  | larger tanks will respond slower | 1+ |  | larger tanks will respond slower | n.a. |  | acts as reservoir (response time very high) | n.a. |  | acts as reservoir (response time very high) | n.a. |  |  | n.a. |  | during phase change, no discernable change in temperature | n.a. |  |  | .
| Suitable storage duration | Range or average value | [days] | 1 to 7 |  |  | 14 to 182.5 |  |  | 14 to 182.5 |  |  | 28 to 182.5 |  |  | 14 to 182.5 |  |  | 182.5 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | 0 to 1 | DELTA_EE_DECC_TES_Final__1_.pdf (publishing.service.gov.uk) | . | 182.5 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | .
Technology specific | Insulation | Range or specific value | [CHF/m2] | 8 | https://www.sciencedirect.com/science/article/pii/S1364032121000472 | glass mineral wool | 8 | https://www.sciencedirect.com/science/article/pii/S1364032121000472 | glass mineral wool | 8 | https://www.sciencedirect.com/science/article/pii/S1364032121000472 | glass mineral wool | - |  | unknown at the moment | - |  | unknown at the moment | - |  | unknown at the moment | - |  |  | - |  | unknown at the moment | .
| Storage temperature range | Range or average value | [°C] | 60 to 180 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | . | 10 to 98 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 10 to 98 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | . | 10 to 80 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 10 to 95 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 10 to 80 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 and http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf | . | 8 to 58 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | range of melting temperatures across 6 LTES systems | 10 to 80 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 and http://task45.iea-shc.org/data/sites/1/publications/IEA_SHC_Task45_B_Report.pdf | . | .
| Charge temperautre range | Range or average value | [°C] | 60 to 180 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | charge and discharge temperatures equal to storage temperatures plus approach temperature in heat exchanger | 10 to 98 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | charge and discharge temperatures equal to storage temperatures plus approach temperature in heat exchanger | 10 to 98 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | charge and discharge temperatures equal to storage temperatures plus approach temperature in heat exchanger | 10 to 80 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 10 to 95 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 60 to 90 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | 8 to 58 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | range of melting temperatures across 6 LTES systems; charge & discharge temperatures subject to heat exchanger approach temperatures | 60 to 90 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | .
| Discharge temeprature range | Range or average value | [°C] | 60 to 180 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | charge and discharge temperatures equal to storage temperatures plus approach temperature in heat exchanger | 10 to 98 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | charge and discharge temperatures equal to storage temperatures plus approach temperature in heat exchanger | 10 to 98 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung | charge and discharge temperatures equal to storage temperatures plus approach temperature in heat exchanger | 10 to 80 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 10 to 95 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | . | 10 to 40 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | 8 to 58 | Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | range of melting temperatures across 6 LTES systems; charge & discharge temperatures subject to heat exchanger approach temperatures | 10 to 40 | https://www.sciencedirect.com/science/article/pii/S0360544222023465 | . | .
| Operational pressure | Range or specific value | [bar] | 0.5-20 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | above atmospheric | 1 atmosphere |  | unpressurised | 1 atmosphere |  | unpressurised | - |  |  | - | [11 empty] | .
| Space requirements | Range or specific value | [m2/m3] | 0.4 - 0.7 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-druckbehaftet.pdf | . | 0.02 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-drucklos.pdf | . | 0.04 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-drucklos.pdf | . | - | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | negligible | 0.10 to 0.15 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdbecken.pdf | . | 0.01 to 0.05 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdsonden.pdf |  |  |  |  | 0.01 to 0.05 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdsonden.pdf |  | .
| wall thickness | Range or specific value | [mm] | 10 to 35 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | steel | 6 to 35 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-drucklos.pdf | steel | 6 to 35 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-drucklos.pdf | steel | 500 to 600 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | well structure, reinforced concrete | 2 to 3 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdbecken.pdf | lining: HDPE: covering made from expanded glass granulate / PEX-Foam | [9 empty] | .
| Thermal losses | Range or average value (tiered by storage temperature) | [W] | n.a. |  | varies with storage temperature and degree of insulation | n.a. |  | varies with storage temperature and degree of insulation | n.a. |  | varies with storage temperature and degree of insulation | n.a. |  |  | n.a. |  | varies with storage temperature and degree of insulation | 0.08*A_top*(T_s-T_a) | Control-oriented modelling and operational optimization of a borehole thermal energy storage - ScienceDirect | assuming convective losses from the top. 0.08 is the heat losses coef, A_top is the top area of the BTES, which can be calculated assuming a cylindrical shape with diameter equal to depth. T_s is the storage temperature and T_a is the ambiente temperature. | negligible |  |  | 0.08*A_top*(T_s-T_a) | Control-oriented modelling and operational optimization of a borehole thermal energy storage - ScienceDirect | assuming convective losses from the top. 0.08 is the heat losses coef, A_top is the top area of the BTES, which can be calculated assuming a cylindrical shape with diameter equal to depth. T_s is the storage temperature and T_a is the ambiente temperature. | .
| insulation thickness | Range or specific value | [mm] | 30 to 50 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stah | mineral wool | 30 to 50 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-drucklos.pdf | mineral wool | 30 to 50 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-stahltank-drucklos.pdf | mineral wool | 250 to 400; 80 to 100 | OST - BigStoreDH – Grosse Wärmespeicher in der Nah- und Fernwärme: Chancen und Business Cases für die Dekarbonisierung & Seasonal thermal energy storage: A techno-economic literature review - ScienceDirect | bore casing, steel or glass fibre reinforced plastic; filter section, stainless steel | 200 to 600 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdbecken.pdf | foam glass ballast | 400 to 800 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdsonden.pdf | upper insulation layer; foam glass ballast |  |  |  | 400 to 800 | https://www.ost.ch/fileadmin/dateiliste/3_forschung_dienstleistung/institute/spf/forschung/projekte/bigstoredh-factsheet-erdsonden.pdf | upper insulation layer; foam glass ballast | .
Emissions | Embodied emissions | Range or average value | [tCO2/MWh stored] | See Remark | https://www.greenspec.co.uk/building-design/embodied-energy/; https://doi.org/10.1016/j.enbuild.2009.06.003 | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (77.44 kgCO2 eq. /m2 For Mineral Wool) | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (77.44 kgCO2 eq. /m2 For Mineral Wool) | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (77.44 kgCO2 eq. /m2 For Mineral Wool) | See Remark | https://www.researchgate.net/publication/274767152_The_carbon_footprint_of_reinforced_concrete | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (0.06-0.47 kgCO2 eq. /kg For Reinforced concrete) | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel for charging and discharing pipes) and insulation materials | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel for charging and discharing pipes, PE/PEX for borehole heat exchangers) and insulation materials (Foam glass ballast); Bentonite suspension used for backfill | See Remark | https://www.sciencedirect.com/science/article/pii/S0306261914006448#s0010 | varies considerably depending on PCM utilised (sodium nitrate embodied energy 16MJ/kg) | 1.16 heating (projected average 0.67 till 2050) 0.0875 cooling (projected average 0.05 till 2050) | Smart Thermal Grids – A Review https://doi.org/10.1515/sbeef-2016-0030 | value is per annum, for heating | .
|  | Range or average value | [kgCO2/kW delivered] | See Remark | https://www.greenspec.co.uk/building-design/embodied-energy/; https://doi.org/10.1016/j.enbuild.2009.06.003 | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (77.44 kgCO2 eq. /m2 For Mineral Wool) | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (77.44 kgCO2 eq. /m2 For Mineral Wool) | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (77.44 kgCO2 eq. /m2 For Mineral Wool) | See Remark | https://legacy.winnipeg.ca/finance/findata/matmgt/documents/2012/682-2012/682-2012_Appendix_H-WSTP_South_End_Plant_Process_Selection_Report/Appendix%207.pdf | largely dependent on construction (6.15 kgCO2/kg Stainless Steel) and insulation materials (0.06-0.47 kgCO2 eq. /kg For Reinforced concrete) | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel for charging and discharing pipes) and insulation materials | See Remark |  | largely dependent on construction (6.15 kgCO2/kg Stainless Steel for charging and discharing pipes, PE/PEX for borehole heat exchangers) and insulation materials (Foam glass ballast); Bentonite suspension used for backfill | See Remark | https://www.sciencedirect.com/science/article/pii/S0306261914006448#s0010 | varies considerably depending on PCM utilised (sodium nitrate embodied energy 16MJ/kg) |  |  |  | .
system depdenent